
[image: image1.png]v 77 mMmagicpak.




SECTION 15700

M-SERIES™ ALL-IN-ONE HVAC SYSTEM

** NOTE TO SPECIFIER ** MagicPak; heating and cooling solutions.
This section is based on the products of MagicPak, which is located at:
215 Metropolitan Dr.  
West Columbia, SC 29170 
Tel: 866-282-7257
Email: MagicPak.Applications@alliedair.com
Web: www.MagicPak.com  
 [ Click Here ] for additional information.
MagicPak All-In-One Units combine heating and cooling in one compact, easy-to-install unit. Because these are ducted units, they are perfect for apartments, condominiums, assisted living, dormitories, and other multiple occupancy buildings.
Professionals who take pride in a building's appearance and expect reliable performance know that MagicPak units are their best choice.
Available in gas heating/electric cooling, heat pump and electric heating/cooling, MagicPak units' features make them the easiest combination heating and cooling you can specify.

PART  1   GENERAL

1.1  
SECTION INCLUDES

** NOTE TO SPECIFIER ** Delete items below not required for project.

A. 
Gas heating/ electric cooling packaged units. (MGE)

B. 
Electric heating/ electric cooling packaged units. (MCE)

C. 
Electric heat pump packaged units with supplementary electric heating. (MHP)

1.2  
RELATED SECTIONS

** NOTE TO SPECIFIER ** Delete any sections below not relevant to this project; add others as required.

A. 
Section 15050 - Common Work Results for HVAC.

B. 
Section 16050 - Common Work Results for Electrical.

1.3  
REFERENCES

** NOTE TO SPECIFIER ** Delete references from the list below that are not actually required by the text of the edited section.

A. 
ANSI/AHRI 210/240-2023: Unitary Small Air Conditioners and Heat Pumps.

1.4  
SUBMITTALS

A. 
Submit under provisions of Section 01300 - Administrative Requirements.

B. 
Product Data: Manufacturer's data sheets on each product to be used, including:

1. 
Preparation instructions and recommendations.

2. 
Storage and handling requirements and recommendations.

3. 
Installation methods.

C. 
Shop Drawings and Wiring Schematics: Provide detailed physical layout and wiring schematics for installation.

1.5  
QUALITY ASSURANCE

A. 
Manufacturer Qualifications: Minimum 5 year experience manufacturing similar products.

B. 
Installer Qualifications: Minimum 2 year experience installing similar products.

** NOTE TO SPECIFIER ** Include a mock-up if the project size and/or quality warrant taking such a precaution. The following is one example of how a mock-up on a large project might be specified. When deciding on the extent of the mock-up, consider all the major different types of work on the project.

C. 
Mock-Up: Provide a mock-up for evaluation of surface preparation techniques and application workmanship.

1. 
Finish areas designated by Architect.

2. 
Do not proceed with remaining work until workmanship is approved by Architect.

3. 
Refinish mock-up area as required to produce acceptable work.

1.6  
PRE-INSTALLATION MEETINGS

A. 
Convene minimum two weeks prior to starting work of this section.

1.7  
DELIVERY, STORAGE, AND HANDLING

A. 
Deliver and store products in manufacturer's unopened packaging bearing the brand name and manufacturer's identification until ready for installation.

B. 
Handle materials as recommended by manufacturer to avoid damage.

1.8  
PROJECT CONDITIONS

A. 
Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results. Do not install products under environmental conditions outside manufacturer's recommended limits.

1.9  
SEQUENCING

A. 
Ensure that products of this section are supplied to affected trades in time to prevent interruption of construction progress.

PART  2   PRODUCTS

2.1  
MANUFACTURERS

A. 
Acceptable Manufacturer: MagicPak, which is located at: 215 Metropolitan Dr.  ; West Columbia, SC 29170 ; Tel: 866-282-7257; Email: MagicPak.Applications@alliedair.com; Web: www.MagicPak.com 

** NOTE TO SPECIFIER ** Delete one of the following two paragraphs; coordinate with requirements of Division 1 section on product options and substitutions.

B. 
Substitutions: Not permitted.

C. 
Requests for substitutions will be considered in accordance with provisions of Section 01600 - Product Requirements.

2.2  
GAS HEATING / ELECTRIC COOLING ALL-IN-ONE UNITS
A. 
MGE8 M-Series Model Units: Gas Heating / Electric Cooling and Residential Packaged Units Single Phase as manufactured by Allied Air Enterprises LLC, A Lennox International Inc. Company.

1. 
Capacity:

** NOTE TO SPECIFIER ** Delete capacity for heating and cooling not required.

a. 
Cooling Capacity: ¾ ton.

b.        Cooling Capacity: 1 ton.

c. 
Cooling Capacity: 1 ½ ton.

d. 
Cooling Capacity: 2 ton.

e. 
Cooling Capacity: 2 ½ ton.

f. 
Cooling Capacity: 3 ton.

g. 
Heating Capacity: 15 kBTUH.

h.        Heating Capacity: 24 kBTUH.

i.         Heating Capacity: 36 kBTUH.

j. 
Heating Capacity: 48 kBTUH.

k. 
Heating Capacity: 60 kBTUH.

2. 
Construction:

a. 
Certified ANSI/AHRI 210/240-2023: Unitary Small Air Conditioners and Heat Pumps.

b. 
From 11.7 SEER2 to 13.4 SEER2 and 10.6 EER2 cooling efficiency.
c. 
Completely self-contained heating and cooling package.

1) 
No outside condensing unit.

2) 
No external refrigerant lines.

3) 
No separate cooling coil.

4) 
No separate venting system.

5) 
No additional drain pan required

d. 
Pre-wired and pre-charged.

e. 
Individually metered and controlled.

f. 
Easy service access.

g. 
Louver color options to match building facade.

h. 
Internal vent system (direct vent).

3. 
Refrigerant System:

a. 
R-454B Refrigerant.

b. 
Rifled copper tubing with lanced fin coils.

4. 
Heat Exchanger:

** NOTE TO SPECIFIER ** Options. Delete material not required.

a. 
Standard stainless-steel heat exchanger.

5. 
Cabinet:

a. 
Galvanized steel cabinet material.

b. 
Fully insulated cabinet for quiet operation.

** NOTE TO SPECIFIER ** Options. Delete options not required.

c. 
Wall sleeve as scheduled or indicated.

d. 
Decorative extruded aluminum louver as scheduled or indicated.

6. 
Blower:
a. 
Five-speed ECM permanently lubricated motor for low maintenance, maximum efficiency and wide airflow range.
b. 
Dynamically balanced blower with resilient motor mounts for smooth and quiet operation.

c. 
Internal washable filter.

d. 
Upgrade MERV 8 filter.

7. 
Controls:

a. 
Color coded wiring for easy service.

b. 
Fuse protection on 24V circuit.
c.         Factory installed refrigerant detection system sensor and control on all units at or above 64 oz. of refrigerant charge.

d.        Optional field-installed refrigerant detection system sensor and control on all units below 64 oz. of refrigerant charge.
8. 
Installation:

a. 
Easy to install and service.

b. 
External utility connections for gas and high and low voltage lines.

c. 
Louver mounts flush to outside wall.

d.        Must be ducted air supply and return to unit – No free air supply/return allowed)

9. 
Warranty:

a. 
5 year limited warranty on all parts.

** NOTE TO SPECIFIER ** Delete heat exchanger warranty not required.

b. 

20 year warranty on stainless steel heat exchanger.
B.       MGE9 M-Series Model Units: Gas Heating / Electric Cooling Single-Package Air Conditioners (SPAC) and Residential Packaged Units Single Phase as manufactured by Allied Air Enterprises LLC, A Lennox International Inc. Company.

1. 
Capacity:

** NOTE TO SPECIFIER ** Delete capacity for heating and cooling not required.

a.       Cooling Capacity: 1 ton.

b.       Cooling Capacity: 1 ½ ton.

c.       Cooling Capacity: 2 ton.

d.       Cooling Capacity: 2 ½ ton.

e.       Heating Capacity: 20 kBTUH. 

f.        Heating Capacity: 30 kBTUH. 

g.       Heating Capacity: 40 kBTUH. 

h.       Heating Capacity: 50 kBTUH.

2.       Construction:

a.      Certified ANSI/AHRI 210/240: Unitary Small Air Conditioners and Heat Pumps.

b. 
From 12 SEER/11.7 SEER2 and 11 EER/10.6 EER2 cooling efficiency.

c. 
Completely self-contained heating and cooling package.

1) 
No outside condensing unit.

2) 
No external refrigerant lines.

3) 
No separate cooling coil.

4) 
No separate venting system.

5) 
No additional drain pan required

d. 
Pre-wired and pre-charged.

e. 
Individually metered and controlled.

f. 
Easy service access.

g. 
Louver color options to match building facade.

h. 
Internal vent system (direct vent).

3.       Refrigerant System:

a. 
  R454-B Refrigerant.

b. 
Rifled copper tubing with lanced fin coils.

4. 
Heat Exchanger:

** NOTE TO SPECIFIER ** Options. Delete material not required.

a.      Standard stainless-steel heat exchanger.

b.      Standard stainless-steel secondary heat exchanger.

5.      Cabinet:

a. 
Galvanized steel cabinet material.

b. 
Fully insulated cabinet for quiet operation.

** NOTE TO SPECIFIER ** Options. Delete options not required.

c. 
Wall sleeve as scheduled or indicated.

d. 
Decorative extruded aluminum louver as scheduled or indicated.

6. 
Blower:

a. 
Five-speed permanently lubricated motor for low maintenance, maximum efficiency and wide airflow range.

b. 
ECM permanently lubricated motor for low maintenance and maximum efficiency.

c. 
Dynamically balanced blower with resilient motor mounts for smooth and quiet operation.

d. 
Internal washable filter.

e. 
Upgrade MERV 8 filter.

7. 
Controls:

a. 
Two-Stage gas heating

b.      Color coded wiring for easy service.

c. 
Fuse protection on 24V circuit.

d.      Factory installed refrigerant detection system sensor and control on all units at or above 64 oz. of refrigerant charge. 

e.      Optional field-installed refrigerant detection system sensor and control on all units below 64 oz. of refrigerant charge

8.
Installation:

a. 
Easy to install and service.

b. 
External utility connections for gas and high and low voltage lines.

c. 
Louver mounts flush to outside wall.

d.      Must be ducted air supply and return to unit – No free air supply/return allowed)

9.
Warranty:

e. 
5 year limited warranty on all parts.

** NOTE TO SPECIFIER ** Delete heat exchanger warranty not required.

f. 
20 year warranty on stainless steel heat exchanger.

1.2  ELECTRIC HEATING/ ELECTRIC COOLING ALL-IN-ONE UNITS
A
MCE M-Series Model Units: Electric Heating / Electric Cooling and Residential Packaged Units Single Phase as manufactured by Allied Air Enterprises LLC, A Lennox International Inc. Company.

1. 
Capacity:

** NOTE TO SPECIFIER ** Delete capacity for heating and cooling not required.

a. 
Cooling Capacity: ¾ ton.

b.        Cooling Capacity: 1 ton.

c. 
Cooling Capacity: 1 ½ ton.

d. 
Cooling Capacity: 2 ton.

e. 
Cooling Capacity: 2 ½ ton.

f.         Cooling Capacity: 3 ton.

g. 
Heating Capacity: 3 kW.

h. 
Heating Capacity: 5 kW.

i. 
Heating Capacity: 7 kW.

j. 
Heating Capacity: 10 kW.

2. 
Construction:

a. 
Certified ANSI/AHRI 210/240-2023: Unitary Small Air Conditioners and Heat Pumps.

b. 
From 11.7 SEER2 to 13.4 SEER2 and 10.6 EER2 cooling efficiency.

c. 
Completely self-contained heating and cooling package.

1) 
No outside condensing unit.

2) 
No external refrigerant lines.

3) 
No separate cooling coil.

4) 
No additional drain pan required
d. 
Pre-wired and pre-charged.

e. 
Individually metered and controlled.

f. 
Easy service access.

g. 
Louver color options to match building facade.

** NOTE TO SPECIFIER ** Options. Delete options not required.

h. 
Optional factory installed ventilation air - up to 15% fresh air.

i. 
Provide No Electric Heat design.

3. 
Refrigerant System:

a. 
R-454B Refrigerant.
b. 
Rifled copper tubing with lanced fin coils.

4. 
Cabinet:

a. 
Fully insulated cabinet for quiet operation.

** NOTE TO SPECIFIER ** Options. Delete options not required.

b. 
Wall sleeve as scheduled or indicated.

c. 
Decorative extruded aluminum louver as scheduled or indicated.

5. 
Blower:

a. 
Five-speed ECM permanently lubricated motor for low maintenance, maximum efficiency and wide airflow range.
b. 
Dynamically balanced blower with resilient motor mounts for smooth and quiet operation.

c. 
Internal washable filter.

d.        Upgrade MERV 8 filter.

6. 
Controls:

a. 
Color coded wiring for easy service.

b. 
Fuse protection on 24V circuit.

c. 
No heat models include 24V output to control external heat source.

d.        Factory installed refrigerant detection system sensor and control on all units at or above 64 oz. of refrigerant charge.

e.        Required field-installed refrigerant detection system sensor and control kit on all units below 64 oz. of refrigerant charge installed in free air return (non ducted air return) configurations.

f.         Optional field-installed refrigerant detection system sensor and control on all units below 64 oz. of refrigerant charge in ducted return air configurations.

7. 
Installation:

a. 
Easy to install and service.

b. 
Louver mounts flush to outside wall.

c. 
External utility connections high and low voltage lines.

d.         Recommended Return air duct connection 

e.         Free Air Return Permitted provided that a refrigerant detection system sensor and control kit are installed

8. 
Warranty:

a. 
5 year limited warranty on all parts.

2.4
ELECTRIC HEAT PUMP ALL-IN-ONE UNITS
B. 
MHP M-Series Model Units: Electric Heat Pump and Residential Packaged Units Single Phase as manufactured by Allied Air Enterprises LLC, A Lennox International Inc. Company.

1. 
Capacity:

** NOTE TO SPECIFIER ** Delete capacity for heating and cooling not required.

a. 
Cooling Capacity: ¾ ton.

b.        Cooling Capacity: 1 ton.

c. 
Cooling Capacity: 1-1/2 ton.

d. 
Cooling Capacity: 2 ton.

e. 
Cooling Capacity: 2-1/2 ton.

f. 
Cooling Capacity: 3 ton.

g. 
Heating Capacity: 3 kW.

h. 
Heating Capacity: 5 kW.

i. 
Heating Capacity: 7 kW.

j. 
Heating Capacity: 10 kW.

2. 
Construction:

a.        Certified ANSI/AHRI 210/240-2023: Unitary Small Air Conditioners and Heat Pumps.

b.        From 11.7 SEER2 to 13.4 SEER2 and 10.6 EER2 cooling efficiency.
c. 
From 6.3 HSPF2 to 6.7 HSPF2 heating efficiency.
d. 
Completely self-contained heating and cooling package.

1) 
No outside condensing unit.

2) 
No external refrigerant lines.

3) 
No separate cooling coil.

4) 
No additional drain pan required

e. 
Pre-wired and pre-charged.

f. 
Individually metered and controlled.

g. 
Easy service access.

h. 
Louver color options to match building facade.

** NOTE TO SPECIFIER ** Option. Delete if not required.

i. 
Optional factory installed ventilation air - up to 15% fresh air.

3. 
Refrigerant System:

a. 
R-454B Refrigerant.
b. 
Rifled copper tubing with lanced fin coils.

4. 
Cabinet:

a. 
Fully insulated cabinet for quiet operation.

** NOTE TO SPECIFIER ** Options. Delete options not required.

b. 
Wall sleeve as scheduled or indicated.

c. 
Decorative extruded aluminum louver as scheduled or indicated.

5. 
Blower:

a. 
Five-speed ECM permanently lubricated motor for low maintenance, maximum efficiency and wide airflow range.

b. 
Dynamically balanced blower with resilient motor mounts for smooth and quiet operation.

c. 
Internal washable filter.

d.        Upgrade MERV 8 filter.

6. 
Controls:

a. 
Color coded wiring for easy service.

b. 
Fuse protection on 24V circuit.

c.         Factory installed refrigerant detection system sensor and control on all units at or above 64 oz. of refrigerant charge.

d.        Required field-installed refrigerant detection system sensor and control kit on all units below 64 oz. of refrigerant charge installed in free air return (non ducted air return) configurations.

e.         Optional field-installed refrigerant detection system sensor and control on all units below 64 oz. of refrigerant charge in ducted return air configurations.

f. .

7. 
Installation:

a. 
Easy to install and service.

b. 
Louver mounts flush to outside wall.

c. 
External utility connections high and low voltage lines.

d.         Recommended Return air duct connection 

e.         Free Air Return Permitted provided that a refrigerant detection system sensor and control kit are installed

8. 
Warranty:

a. 
5 year limited warranty on all parts.

PART  2   EXECUTION

2.1  
EXAMINATION

A. 
Do not begin installation until wall openings and rough-in have been properly prepared.

B. 
If preparation is the responsibility of another installer, notify Architect of unsatisfactory preparation before proceeding.

2.2  
PREPARATION

A. 
Prepare conditions using the methods recommended by the manufacturer for achieving the best result for the operation under the project conditions.

2.3  
INSTALLATION

A. 
Install in accordance with manufacturer's instructions. Test for proper operation and adjust as required until satisfactory results are obtained.

2.4  
PROTECTION

A. 
Protect installed products until completion of project.

B. 
Touch-up, repair or replace damaged products before Substantial Completion.

END OF SECTION

15700-1 

